## Overview
Seplos BMS v3
## Modbus RTU
Seplos BMS v3 uses modbus RTU protocol for reading and writing the values and settings as seen in the BMSSudio app
The individual BMSses can be addressed by the modbus Client Id. (minus 1: Client 1 in software = client id 0 in modbus)
Settings:
speed: 19200 8N1
## Main blocks
Block | adres | Length | len(hex) | Type | Description
PIA | 0x1000 | 18 | 0x12 | registers | Basic status info
PIB | 0x1100 | 26 | 0x1A | registers | Cell voltage and temperatures
PIC | 0x1200 | 144 | 0x90 | bits | Cell & other Alarms
SPA | 0x1300 | 106 | 0x6A | registers | Settings
SFA | 0x1400 | 80 | 0x50 | bits | Overall alarms
SCA | 0x150D | 13 | 0x0D | registers | FET and onther status & setting
| 0x1700 | 51 | 0x33 | registers | Manufacturer, product and serialnumber info
Request made by Seplos software and example response
client.read_input_registers(0x1700, 0x33, slave=0):
response: [22618, 18477, 17772, 25955, 21605, 25448, 8259, 28462, 11340, 29796, 16973, 21297, 13907, 12848, 12353, 11603, 20528, 13634, 0, 0, 12595, 21328, 12341, 16946, 13105, 12594, 13872, 12342, 12546, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0, 0]
response (hex): 585a482d456c65635465636820436f2e2c4c7464424d53313653323030412d5350303542003133535030354232333131323630303633000000000000000000000000
string: XZH-ElecTech Co.,LtdBMS16S200A-SP05B13SP05B2311260063
client.read_input_registers(0x1301, 0x01, slave=0):
response: [16]
response (hex): 10
client.read_input_registers(0x1000, 0x12, slave=0):
response: [5236, 1301, 3800, 30400, 64, 125, 1000, 2, 3272, 2837, 3275, 3268, 2845, 2831, 0, 180, 180, 1000]
response (hex): 1474515ed876c0407d3e82cc8b15ccbcc4b1db0f0b4b43e8
client.read_input_registers(0x1100, 0x1a, slave=0):
response: [3273, 3273, 3268, 3272, 3274, 3274, 3275, 3275, 3274, 3273, 3273, 3270, 3271, 3271, 3270, 3272, 2842, 2833, 2831, 2845, 2731, 2731, 2731, 2731, 2833, 2829]
response (hex): cc9cc9cc4cc8ccaccaccbccbccacc9cc9cc6cc7cc7cc6cc8b1ab11b0fb1daabaabaabaabb11b0d
client.read_input_registers(0x1300, 0x6a, slave=0):
response: [4, 16, 5400, 5600, 5400, 5760, 4800, 4640, 4800, 4320, 3400, 3500, 3400, 3650, 3100, 2900, 3100, 2700, 2000, 1000, 500, 203, 205, 210, 100, 300, 300, 65333, 65331, 65326, 100, 65186, 300, 65236, 106, 600, 5, 3000, 205, 10, 3500, 3400, 1500, 1000, 800, 200, 30, 3201, 3231, 3231, 3281, 2781, 2751, 2731, 2631, 3231, 3281, 3281, 3331, 2761, 2631, 2731, 2581, 3201, 3231, 3281, 3331, 2761, 2731, 2731, 2631, 3581, 3681, 3581, 3831, 2831, 2731, 3231, 2731, 10, 3400, 50, 30, 960, 150, 100, 70, 50, 30400, 30400, 3800, 48, 60, 240, 10, 7, 0, 13, 0, 500, 300, 5760, 180, 65356, 5, 8]
response (hex): 410151815e01518168012c0122012c010e0d48dacd48e42c1cb54c1ca8c7d03e81f4cbcdd26412c12cff35ff33ff2e64fea212cfed46a2585bb8cdadacd485dc3e8320c81ec81c9fc9fcd1addabfaaba47c9fcd1cd1d03ac9a47aaba15c81c9fcd1d03ac9aabaaba47dfde61dfdef7b0faabc9faabad48321e3c09664463276c076c0ed8303cf0a70d01f412c1680b4ff4c58
client.read_input_registers(0x1500, 0x04, slave=0):
response: [59399, 776, 4141, 7710]
response (hex): e807308102d1e1e
client.read_coils(0x1200, 0x90, slave=0):
response: [False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, True, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, True, True, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False, False]
client.read_coils(0x1400, 0x50, slave=0):
response: [True, True, True, True, True, True, True, True, True, True, True, True, True, True, True, True, True, True, True, True, True, True, False, False, True, False, False, False, False, False, False, False, True, True, True, True, True, True, True, False, True, True, True, True, False, True, False, False, True, True, True, True, True, False, False, True, True, True, True, True, False, False, False, False, True, True, False, False, False, True, True, False, True, True, True, True, False, True, True, False]
This content © 2023 is licensed under [CC BY-NC 4.0](https://creativecommons.org/licenses/by-nc-sa/4.0/)](https://creativecommons.org/licenses/by-nc-sa/4.0/) ![](img/svg/by-nc.eu.svg)

## PIA
ID | rtuAddress | description zh-CN | description en-US | byte | byteIndex | unit | scale | hasSign | isDisplay | datatype | inHistory
1 | 1000 | 总电压 | Battery voltage | 2 | 0 | V | 0.01 | 0 | 1 | MainInfo | 1
2 | 1001 | 总电流 | Current | 2 | 2 | A | 0.01 | 1 | 1 | MainInfo | 1
3 | 1002 | 剩余容量 | Remaining capacity | 2 | 4 | Ah | 0.01 | 0 | 1 | OtherInfo | 1
4 | 1003 | 总容量 | Total capacity | 2 | 6 | Ah | 0.01 | 0 | 1 | OtherInfo | 0
5 | 1004 | 总放电容量 | Total discharge capacity | 2 | 8 | Ah | 10 | 0 | 1 | OtherInfo | 0
6 | 1005 | SOC | SOC | 2 | 10 | % | 0.1 | 0 | 1 | MainInfo | 0
7 | 1006 | SOH | SOH | 2 | 12 | % | 0.1 | 0 | 1 | OtherInfo | 0
8 | 1007 | 循环次数 | Cycle | 2 | 14 | times | 1 | 0 | 1 | OtherInfo | 0
9 | 1008 | 平均电芯电压 | Averag of cell votage | 2 | 16 | V | 0.001 | 0 | 1 | MainInfo | 0
10 | 1009 | 平均电芯温度 | Averag of cell temperature | 2 | 18 | ℃ | 0.1 | 0 | 1 | OtherInfo | 0
11 | 100A | 最高电芯电压 | Max cell voltage | 2 | 20 | V | 0.001 | 0 | 1 | MainInfo | 0
12 | 100B | 最低电芯电压 | Min cell voltage | 2 | 22 | V | 0.001 | 0 | 1 | MainInfo | 0
13 | 100C | 最高电芯温度 | Max cell temperature | 2 | 24 | ℃ | 0.1 | 0 | 1 | OtherInfo | 0
14 | 100D | 最低电芯温度 | Min cell temperature | 2 | 26 | ℃ | 0.1 | 0 | 1 | OtherInfo | 0
15 | 100E | 系统事件概要 | System events | 2 | 28 |  | 1 | 0 | 0 | OtherInfo | 0
16 | 100F | 建议最大放电电流 | Max discharge current | 2 | 30 | A | 1 | 0 | 1 | OtherInfo | 0
17 | 1010 | 建议最大充电电流 | Max charge current | 2 | 32 | A | 1 | 0 | 1 | OtherInfo | 0
18 | 1011 | 母线电压 | Extern voltage | 2 | 34 | V | 0.001 | 0 | 0 | OtherInfo | 0

## PIB
ID | rtuAddress | description zh-CN | description en-US | byte | byteIndex | unit | scale | hasSign | isDisplay | datatype | inHistory
1 | 1100 | 电芯01 | Cell01 | 2 | 0 | V | 0.001 | 0 | 1 | CellInfo | 1
2 | 1101 | 电芯02 | Cell02 | 2 | 2 | V | 0.001 | 0 | 1 | CellInfo | 1
3 | 1102 | 电芯03 | Cell03 | 2 | 4 | V | 0.001 | 0 | 1 | CellInfo | 1
4 | 1103 | 电芯04 | Cell04 | 2 | 6 | V | 0.001 | 0 | 1 | CellInfo | 1
5 | 1104 | 电芯05 | Cell05 | 2 | 8 | V | 0.001 | 0 | 1 | CellInfo | 1
6 | 1105 | 电芯06 | Cell06 | 2 | 10 | V | 0.001 | 0 | 1 | CellInfo | 1
7 | 1106 | 电芯07 | Cell07 | 2 | 12 | V | 0.001 | 0 | 1 | CellInfo | 1
8 | 1107 | 电芯08 | Cell08 | 2 | 14 | V | 0.001 | 0 | 1 | CellInfo | 1
9 | 1108 | 电芯09 | Cell09 | 2 | 16 | V | 0.001 | 0 | 1 | CellInfo | 1
10 | 1109 | 电芯10 | Cell10 | 2 | 18 | V | 0.001 | 0 | 1 | CellInfo | 1
11 | 110A | 电芯11 | Cell11 | 2 | 20 | V | 0.001 | 0 | 1 | CellInfo | 1
12 | 110B | 电芯12 | Cell12 | 2 | 22 | V | 0.001 | 0 | 1 | CellInfo | 1
13 | 110C | 电芯13 | Cell13 | 2 | 24 | V | 0.001 | 0 | 1 | CellInfo | 1
14 | 110D | 电芯14 | Cell14 | 2 | 26 | V | 0.001 | 0 | 1 | CellInfo | 1
15 | 110E | 电芯15 | Cell15 | 2 | 28 | V | 0.001 | 0 | 1 | CellInfo | 1
16 | 110F | 电芯16 | Cell16 | 2 | 30 | V | 0.001 | 0 | 1 | CellInfo | 1
17 | 1110 | 电池温度1 | Cell temperature 1 | 2 | 32 | ℃ | 0.1 | 0 | 1 | OtherInfo | 1
18 | 1111 | 电池温度2 | Cell temperature 2 | 2 | 34 | ℃ | 0.1 | 0 | 1 | OtherInfo | 1
19 | 1112 | 电池温度3 | Cell temperature 3 | 2 | 36 | ℃ | 0.1 | 0 | 1 | OtherInfo | 1
20 | 1113 | 电池温度4 | Cell temperature 4 | 2 | 38 | ℃ | 0.1 | 0 | 1 | OtherInfo | 1
21 | 1114 | 电池温度5 | Cell temperature 5 | 2 | 40 | ℃ | 0.1 | 0 | 0 | OtherInfo | 1
22 | 1115 | 电池温度6 | Cell temperature 6 | 2 | 42 | ℃ | 0.1 | 0 | 0 | OtherInfo | 1
23 | 1116 | 电池温度7 | Cell temperature 7 | 2 | 44 | ℃ | 0.1 | 0 | 0 | OtherInfo | 1
24 | 1117 | 电池温度8 | Cell temperature 8 | 2 | 46 | ℃ | 0.1 | 0 | 0 | OtherInfo | 1
25 | 1118 | 环境温度 | Ambient temperature | 2 | 48 | ℃ | 0.1 | 0 | 1 | OtherInfo | 1
26 | 1119 | 功率温度 | Power temperature | 2 | 50 | ℃ | 0.1 | 0 | 1 | OtherInfo | 1

## PIC
ID | rtuAddress | description zh-CN | description en-US | bit | bitIndex | byteIndex | linkAddress | isDisplay | datatype | attribute | inHistory
1 | 1200 | 电芯01电压低 | Cells voltage 01 low alarm state | 1 | 0 | 0 | 1100 | 0 | CellStatus | Under | 0
2 | 1201 | 电芯02电压低 | Cells voltage 02 low alarm state | 1 | 1 | 0 | 1101 | 0 | CellStatus | Under | 0
3 | 1202 | 电芯03电压低 | Cells voltage 03 low alarm state | 1 | 2 | 0 | 1102 | 0 | CellStatus | Under | 0
4 | 1203 | 电芯04电压低 | Cells voltage 04 low alarm state | 1 | 3 | 0 | 1103 | 0 | CellStatus | Under | 0
5 | 1204 | 电芯05电压低 | Cells voltage 05 low alarm state | 1 | 4 | 0 | 1104 | 0 | CellStatus | Under | 0
6 | 1205 | 电芯06电压低 | Cells voltage 06 low alarm state | 1 | 5 | 0 | 1105 | 0 | CellStatus | Under | 0
7 | 1206 | 电芯07电压低 | Cells voltage 07 low alarm state | 1 | 6 | 0 | 1106 | 0 | CellStatus | Under | 0
8 | 1207 | 电芯08电压低 | Cells voltage 08 low alarm state | 1 | 7 | 0 | 1107 | 0 | CellStatus | Under | 0
9 | 1208 | 电芯09电压低 | Cells voltage 09 low alarm state | 1 | 0 | 1 | 1108 | 0 | CellStatus | Under | 0
10 | 1209 | 电芯10电压低 | Cells voltage 10 low alarm state | 1 | 1 | 1 | 1109 | 0 | CellStatus | Under | 0
11 | 120A | 电芯11电压低 | Cells voltage 11 low alarm state | 1 | 2 | 1 | 110A | 0 | CellStatus | Under | 0
12 | 120B | 电芯12电压低 | Cells voltage 12 low alarm state | 1 | 3 | 1 | 110B | 0 | CellStatus | Under | 0
13 | 120C | 电芯13电压低 | Cells voltage 13 low alarm state | 1 | 4 | 1 | 110C | 0 | CellStatus | Under | 0
14 | 120D | 电芯14电压低 | Cells voltage 14 low alarm state | 1 | 5 | 1 | 110D | 0 | CellStatus | Under | 0
15 | 120E | 电芯15电压低 | Cells voltage 15 low alarm state | 1 | 6 | 1 | 110E | 0 | CellStatus | Under | 0
16 | 120F | 电芯16电压低 | Cells voltage 16 low alarm state | 1 | 7 | 1 | 110F | 0 | CellStatus | Under | 0
17 | 1210 | 电芯01电压高 | Cells voltage 01 high alarm state | 1 | 0 | 2 | 1100 | 0 | CellStatus | Over | 0
18 | 1211 | 电芯02电压高 | Cells voltage 02 high alarm state | 1 | 1 | 2 | 1101 | 0 | CellStatus | Over | 0
19 | 1212 | 电芯03电压高 | Cells voltage 03 high alarm state | 1 | 2 | 2 | 1102 | 0 | CellStatus | Over | 0
20 | 1213 | 电芯04电压高 | Cells voltage 04 high alarm state | 1 | 3 | 2 | 1103 | 0 | CellStatus | Over | 0
21 | 1214 | 电芯05电压高 | Cells voltage 05 high alarm state | 1 | 4 | 2 | 1104 | 0 | CellStatus | Over | 0
22 | 1215 | 电芯06电压高 | Cells voltage 06 high alarm state | 1 | 5 | 2 | 1105 | 0 | CellStatus | Over | 0
23 | 1216 | 电芯07电压高 | Cells voltage 07 high alarm state | 1 | 6 | 2 | 1106 | 0 | CellStatus | Over | 0
24 | 1217 | 电芯08电压高 | Cells voltage 08 high alarm state | 1 | 7 | 2 | 1107 | 0 | CellStatus | Over | 0
25 | 1218 | 电芯09电压高 | Cells voltage 09 high alarm state | 1 | 0 | 3 | 1108 | 0 | CellStatus | Over | 0
26 | 1219 | 电芯10电压高 | Cells voltage 10 high alarm state | 1 | 1 | 3 | 1109 | 0 | CellStatus | Over | 0
27 | 121A | 电芯11电压高 | Cells voltage 11 high alarm state | 1 | 2 | 3 | 110A | 0 | CellStatus | Over | 0
28 | 121B | 电芯12电压高 | Cells voltage 12 high alarm state | 1 | 3 | 3 | 110B | 0 | CellStatus | Over | 0
29 | 121C | 电芯13电压高 | Cells voltage 13 high alarm state | 1 | 4 | 3 | 110C | 0 | CellStatus | Over | 0
30 | 121D | 电芯14电压高 | Cells voltage 14 high alarm state | 1 | 5 | 3 | 110D | 0 | CellStatus | Over | 0
31 | 121E | 电芯15电压高 | Cells voltage 15 high alarm state | 1 | 6 | 3 | 110E | 0 | CellStatus | Over | 0
32 | 121F | 电芯16电压高 | Cells voltage 16 high alarm state | 1 | 7 | 3 | 110F | 0 | CellStatus | Over | 0
33 | 1220 | 电芯温度01低 | Cell temperature 01 low alarm state | 1 | 0 | 4 | 1110 | 0 | TempStatus | Under | 0
34 | 1221 | 电芯温度02低 | Cell temperature 02 low alarm state | 1 | 1 | 4 | 1111 | 0 | TempStatus | Under | 0
35 | 1222 | 电芯温度03低 | Cell temperature 03 low alarm state | 1 | 2 | 4 | 1112 | 0 | TempStatus | Under | 0
36 | 1223 | 电芯温度04低 | Cell temperature 04 low alarm state | 1 | 3 | 4 | 1113 | 0 | TempStatus | Under | 0
37 | 1224 | 电芯温度05低 | Cell temperature 05 low alarm state | 1 | 4 | 4 | 1114 | 0 | TempStatus | Under | 0
38 | 1225 | 电芯温度06低 | Cell temperature 06 low alarm state | 1 | 5 | 4 | 1115 | 0 | TempStatus | Under | 0
39 | 1226 | 电芯温度07低 | Cell temperature 07 low alarm state | 1 | 6 | 4 | 1116 | 0 | TempStatus | Under | 0
40 | 1227 | 电芯温度08低 | Cell temperature 08 low alarm state | 1 | 7 | 4 | 1117 | 0 | TempStatus | Under | 0
41 | 1228 | 电芯温度01高 | Cell temperature 01 high alarm state | 1 | 0 | 5 | 1110 | 0 | TempStatus | Over | 0
42 | 1229 | 电芯温度02高 | Cell temperature 02 high alarm state | 1 | 1 | 5 | 1111 | 0 | TempStatus | Over | 0
43 | 122A | 电芯温度03高 | Cell temperature 03 high alarm state | 1 | 2 | 5 | 1112 | 0 | TempStatus | Over | 0
44 | 122B | 电芯温度04高 | Cell temperature 04 high alarm state | 1 | 3 | 5 | 1113 | 0 | TempStatus | Over | 0
45 | 122C | 电芯温度05高 | Cell temperature 05 high alarm state | 1 | 4 | 5 | 1114 | 0 | TempStatus | Over | 0
46 | 122D | 电芯温度06高 | Cell temperature 06 high alarm state | 1 | 5 | 5 | 1115 | 0 | TempStatus | Over | 0
47 | 122E | 电芯温度07高 | Cell temperature 07 high alarm state | 1 | 6 | 5 | 1116 | 0 | TempStatus | Over | 0
48 | 122F | 电芯温度08高 | Cell temperature 08 high alarm state | 1 | 7 | 5 | 1117 | 0 | TempStatus | Over | 0
49 | 1230 | 电芯01均衡 | Cell 01 equalization event code | 1 | 0 | 6 | 1100 | 0 | CellStatus | Normal | 0
50 | 1231 | 电芯02均衡 | Cell 02 equalization event code | 1 | 1 | 6 | 1101 | 0 | CellStatus | Normal | 0
51 | 1232 | 电芯03均衡 | Cell 03 equalization event code | 1 | 2 | 6 | 1102 | 0 | CellStatus | Normal | 0
52 | 1233 | 电芯04均衡 | Cell 04 equalization event code | 1 | 3 | 6 | 1103 | 0 | CellStatus | Normal | 0
53 | 1234 | 电芯05均衡 | Cell 05 equalization event code | 1 | 4 | 6 | 1104 | 0 | CellStatus | Normal | 0
54 | 1235 | 电芯06均衡 | Cell 06 equalization event code | 1 | 5 | 6 | 1105 | 0 | CellStatus | Normal | 0
55 | 1236 | 电芯07均衡 | Cell 07 equalization event code | 1 | 6 | 6 | 1106 | 0 | CellStatus | Normal | 0
56 | 1237 | 电芯08均衡 | Cell 08 equalization event code | 1 | 7 | 6 | 1107 | 0 | CellStatus | Normal | 0
57 | 1238 | 电芯09均衡 | Cell 09 equalization event code | 1 | 0 | 7 | 1108 | 0 | CellStatus | Normal | 0
58 | 1239 | 电芯10均衡 | Cell 10 equalization event code | 1 | 1 | 7 | 1109 | 0 | CellStatus | Normal | 0
59 | 123A | 电芯11均衡 | Cell 11 equalization event code | 1 | 2 | 7 | 110A | 0 | CellStatus | Normal | 0
60 | 123B | 电芯12均衡 | Cell 12 equalization event code | 1 | 3 | 7 | 110B | 0 | CellStatus | Normal | 0
61 | 123C | 电芯13均衡 | Cell 13 equalization event code | 1 | 4 | 7 | 110C | 0 | CellStatus | Normal | 0
62 | 123D | 电芯14均衡 | Cell 14 equalization event code | 1 | 5 | 7 | 110D | 0 | CellStatus | Normal | 0
63 | 123E | 电芯15均衡 | Cell 15 equalization event code | 1 | 6 | 7 | 110E | 0 | CellStatus | Normal | 0
64 | 123F | 电芯16均衡 | Cell 16 equalization event code | 1 | 7 | 7 | 110F | 0 | CellStatus | Normal | 0
65 | 1240 | 放电 | Discharge | 1 | 0 | 8 | 1240 | 1 | ModeInfo | Normal | 1
66 | 1241 | 充电 | Charge | 1 | 1 | 8 | 1241 | 1 | ModeInfo | Normal | 1
67 | 1242 | 浮充 | Floating charge | 1 | 2 | 8 | 1242 | 1 | ModeInfo | Normal | 1
68 | 1243 | 满充 | Full charge | 1 | 3 | 8 | 1243 | 1 | ModeInfo | Normal | 1
69 | 1244 | 待机 | Standby mode | 1 | 4 | 8 | 1244 | 1 | ModeInfo | Normal | 1
70 | 1245 | 关机 | Turn off | 1 | 5 | 8 | 1245 | 1 | ModeInfo | Normal | 1
71 | 1246 | 保留 | Reservation | 1 | 6 | 8 | 1246 | 0 | ModeInfo | Normal | 1
72 | 1247 | 保留 | Reservation | 1 | 7 | 8 | 1247 | 0 | ModeInfo | Normal | 1
73 | 1248 | 单体高压告警 | Cell high voltage alarm | 1 | 0 | 9 | 1248 | 1 | OtherStatusInfo | Warn | 1
74 | 1249 | 单体过压保护 | Cell over voltage protection | 1 | 1 | 9 | 1249 | 1 | OtherStatusInfo | Protect | 1
75 | 124A | 单体低压告警 | Cell low voltage alarm | 1 | 2 | 9 | 124A | 1 | OtherStatusInfo | Warn | 1
76 | 124B | 单体欠压保护 | Cell under voltage protection | 1 | 3 | 9 | 124B | 1 | OtherStatusInfo | Protect | 1
77 | 124C | 总压高压告警 | Battery high voltage alarm | 1 | 4 | 9 | 124C | 1 | OtherStatusInfo | Warn | 1
78 | 124D | 总压过压保护 | Battery over voltage protection | 1 | 5 | 9 | 124D | 1 | OtherStatusInfo | Protect | 1
79 | 124E | 总压低压告警 | Battery low voltage alarm | 1 | 6 | 9 | 124E | 1 | OtherStatusInfo | Warn | 1
80 | 124F | 总压欠压保护 | Battery under voltage protection | 1 | 7 | 9 | 124F | 1 | OtherStatusInfo | Protect | 1
81 | 1250 | 充电高温告警 | Charge high temperature alarm | 1 | 0 | 10 | 1250 | 1 | OtherStatusInfo | Warn | 1
82 | 1251 | 充电过温保护 | Charge over temperature protection | 1 | 1 | 10 | 1251 | 1 | OtherStatusInfo | Protect | 1
83 | 1252 | 充电低温告警 | Charge low temperature alarm | 1 | 2 | 10 | 1252 | 1 | OtherStatusInfo | Warn | 1
84 | 1253 | 充电欠温保护 | Charge under temperature protection | 1 | 3 | 10 | 1253 | 1 | OtherStatusInfo | Protect | 1
85 | 1254 | 放电高温告警 | Discharge high temperature alarm | 1 | 4 | 10 | 1254 | 1 | OtherStatusInfo | Warn | 1
86 | 1255 | 放电过温保护 | Discharge over temperature protection | 1 | 5 | 10 | 1255 | 1 | OtherStatusInfo | Protect | 1
87 | 1256 | 放电低温告警 | Discharge low temperature alarm | 1 | 6 | 10 | 1256 | 1 | OtherStatusInfo | Warn | 1
88 | 1257 | 放电欠温保护 | Discharge under temperature protection | 1 | 7 | 10 | 1257 | 1 | OtherStatusInfo | Protect | 1
89 | 1258 | 环境高温告警 | High ambient temperature alarm | 1 | 0 | 11 | 1258 | 1 | OtherStatusInfo | Warn | 1
90 | 1259 | 环境过温保护 | Over ambient temperature protection | 1 | 1 | 11 | 1259 | 1 | OtherStatusInfo | Protect | 1
91 | 125A | 环境低温告警 | Low ambient temperature alarm | 1 | 2 | 11 | 125A | 1 | OtherStatusInfo | Warn | 1
92 | 125B | 环境欠温保护 | Under ambient temperature protection | 1 | 3 | 11 | 125B | 1 | OtherStatusInfo | Protect | 1
93 | 125C | 功率高温告警 | High power temperature alarm | 1 | 4 | 11 | 125C | 1 | OtherStatusInfo | Warn | 1
94 | 125D | 功率过温保护 | Over power temperature protection | 1 | 5 | 11 | 125D | 1 | OtherStatusInfo | Protect | 1
95 | 125E | 电芯低温加热 | Cell temperature low heating | 1 | 6 | 11 | 125E | 1 | OtherStatusInfo | Warn | 1
96 | 125F | 保留 | Reservation | 1 | 7 | 11 | 125F | 0 | OtherStatusInfo | Normal | 1
97 | 1260 | 充电电流告警 | Charge current alarm | 1 | 0 | 12 | 1260 | 1 | OtherStatusInfo | Warn | 1
98 | 1261 | 充电过流保护 | Charge over current protection | 1 | 1 | 12 | 1261 | 1 | OtherStatusInfo | Protect | 1
99 | 1262 | 充电过流二级保护 | Secondary charge over current protection | 1 | 2 | 12 | 1262 | 1 | OtherStatusInfo | Protect | 1
100 | 1263 | 放电电流告警 | Discharge current alarm | 1 | 3 | 12 | 1263 | 1 | OtherStatusInfo | Warn | 1
101 | 1264 | 放电过流保护 | Discharge over current protection | 1 | 4 | 12 | 1264 | 1 | OtherStatusInfo | Protect | 1
102 | 1265 | 放电二级过流保护 | Secondary discharge over current protection | 1 | 5 | 12 | 1265 | 1 | OtherStatusInfo | Protect | 1
103 | 1266 | 输出短路保护 | Output short-circuit protection | 1 | 6 | 12 | 1266 | 1 | OtherStatusInfo | Protect | 1
104 | 1267 | 保留 | Reservation | 1 | 7 | 12 | 1267 | 0 | OtherStatusInfo | Normal | 1
105 | 1268 | 输出短路锁定 | Output short-circuit lock | 1 | 0 | 13 | 1268 | 1 | OtherStatusInfo | Protect | 1
106 | 1269 | 反接保护 | Inverse current protection | 1 | 1 | 13 | 1269 | 0 | OtherStatusInfo | Protect | 1
107 | 126A | 充电二级过流锁定 | Secondary charge over current lock | 1 | 2 | 13 | 126A | 1 | OtherStatusInfo | Protect | 1
108 | 126B | 放电二级过流锁定 | Secondary discharge over current lock | 1 | 3 | 13 | 126B | 1 | OtherStatusInfo | Protect | 1
109 | 126C | 保留 | Reservation | 1 | 4 | 13 | 126C | 0 | OtherStatusInfo | Normal | 1
110 | 126D | 保留 | Reservation | 1 | 5 | 13 | 126D | 0 | OtherStatusInfo | Normal | 1
111 | 126E | 零点未校准 | Zero point uncalibrated | 1 | 6 | 13 | 126E | 1 | OtherStatusInfo | Warn | 1
112 | 126F | 保留 | Reservation | 1 | 7 | 13 | 126F | 0 | OtherStatusInfo | Normal | 1
113 | 1270 | 保留 | Reservation | 1 | 0 | 14 | 1270 | 0 | OtherStatusInfo | Normal | 1
114 | 1271 | 保留 | Reservation | 1 | 1 | 14 | 1271 | 0 | OtherStatusInfo | Normal | 1
115 | 1272 | Soc告警 | SOC alarm | 1 | 2 | 14 | 1272 | 1 | OtherStatusInfo | Warn | 1
116 | 1273 | Soc保护 | SOC protection | 1 | 3 | 14 | 1273 | 1 | OtherStatusInfo | Protect | 1
117 | 1274 | 电芯压差告警 | Cell diff alarm | 1 | 4 | 14 | 1274 | 1 | OtherStatusInfo | Warn | 1
118 | 1275 | 保留 | Reservation | 1 | 5 | 14 | 1275 | 0 | OtherStatusInfo | Normal | 1
119 | 1276 | 保留 | Reservation | 1 | 6 | 14 | 1276 | 0 | OtherStatusInfo | Normal | 1
120 | 1277 | 保留 | Reservation | 1 | 7 | 14 | 1277 | 0 | OtherStatusInfo | Normal | 1
121 | 1278 | 放电开关开启 | Discharge FET on | 1 | 0 | 15 | 1510 | 1 | ControlStatusInfo | Normal | 0
122 | 1279 | 充电开关开启 | Charge FET on | 1 | 1 | 15 | 1511 | 1 | ControlStatusInfo | Normal | 0
123 | 127A | 限流开关开启 | Current limiting FET on | 1 | 2 | 15 | 1512 | 1 | ControlStatusInfo | Normal | 0
124 | 127B | 温度调节开启 | Temp. regulate FET on | 1 | 3 | 15 | 1514 | 1 | ControlStatusInfo | Normal | 0
125 | 127C | 保留 | Reservation | 1 | 4 | 15 | 127C | 0 | ControlStatusInfo | Normal | 0
126 | 127D | 保留 | Reservation | 1 | 5 | 15 | 127D | 0 | ControlStatusInfo | Normal | 0
127 | 127E | 保留 | Reservation | 1 | 6 | 15 | 127E | 0 | ControlStatusInfo | Normal | 0
128 | 127F | 保留 | Reservation | 1 | 7 | 15 | 127F | 0 | ControlStatusInfo | Normal | 0
129 | 1280 | 均衡模块开启 | Equilibrium module to open | 1 | 0 | 16 | 1280 | 1 | ControlStatusInfo | Normal | 1
130 | 1281 | 静态均衡指示 | Static equilibrium indicate | 1 | 1 | 16 | 1281 | 1 | ControlStatusInfo | Normal | 1
131 | 1282 | 静态均衡超时 | Static equilibrium overtime | 1 | 2 | 16 | 1282 | 1 | OtherStatusInfo | Warn | 1
132 | 1283 | 超温禁止均衡 | Equalization temperature limit | 1 | 3 | 16 | 1283 | 1 | ControlStatusInfo | Normal | 1
133 | 1284 | 电芯失效告警 | Cell failure alarm | 1 | 4 | 16 | 1284 | 1 | OtherStatusInfo | Warn | 1
134 | 1285 | 保留 | Reservation | 1 | 5 | 16 | 1285 | 0 | OtherStatusInfo | Normal | 1
135 | 1286 | 保留 | Reservation | 1 | 6 | 16 | 1286 | 0 | OtherStatusInfo | Normal | 1
136 | 1287 | 保留 | Reservation | 1 | 7 | 16 | 1287 | 0 | OtherStatusInfo | Normal | 1
137 | 1288 | NTC失效 | NTC failure | 1 | 0 | 17 | 1288 | 1 | OtherStatusInfo | Protect | 1
138 | 1289 | AFE失效 | AFE failure | 1 | 1 | 17 | 1289 | 1 | OtherStatusInfo | Protect | 1
139 | 128A | 充电管失效 | Charge mosfets failure | 1 | 2 | 17 | 128A | 1 | OtherStatusInfo | Protect | 1
140 | 128B | 放电管失效 | Discharge mosfets failure | 1 | 3 | 17 | 128B | 1 | OtherStatusInfo | Protect | 1
141 | 128C | 电芯压差失效 | Celldiff failure | 1 | 4 | 17 | 128C | 1 | OtherStatusInfo | Protect | 1
142 | 128D | 断线失效 | Break line failure | 1 | 5 | 17 | 128D | 0 | OtherStatusInfo | Protect | 1
143 | 128E | 按键失效 | Key failure | 1 | 6 | 17 | 128E | 0 | OtherStatusInfo | Protect | 1
144 | 128F | 气溶胶报警 | Aerosol alarm | 1 | 7 | 17 | 128F | 1 | OtherStatusInfo | Protect | 1

## SPA
ID | rtuAddress | description zh-CN | description en-US | byte | value | Index | unit | scale | hasSign | isDisplay | datatype | attribute
1 | 1300 | 电芯温度数目 | Ntc number | 2 | 0 | 0 | num | 1 | 0 | 1 | IntParameterInfo | Normal
2 | 1301 | 串联电池节数 | Serial battery number | 2 | 0 | 2 | num | 1 | 0 | 1 | IntParameterInfo | Normal
3 | 1302 | 总压高压恢复 | Battery high voltage recovery | 2 | 0 | 4 | V | 0.01 | 0 | 1 | IntParameterInfo | Normal
4 | 1303 | 总压高压告警 | Battery high voltage alarm | 2 | 0 | 6 | V | 0.01 | 0 | 1 | IntParameterInfo | Normal
5 | 1304 | 总压过压恢复 | Battery over voltage recovery | 2 | 0 | 8 | V | 0.01 | 0 | 1 | IntParameterInfo | Normal
6 | 1305 | 总压过压保护 | Battery over voltage protection | 2 | 0 | 10 | V | 0.01 | 0 | 1 | IntParameterInfo | Normal
7 | 1306 | 总压低压恢复 | Battery low voltage recovery | 2 | 0 | 12 | V | 0.01 | 0 | 1 | IntParameterInfo | Normal
8 | 1307 | 总压低压告警 | Battery low voltage alarm | 2 | 0 | 14 | V | 0.01 | 0 | 1 | IntParameterInfo | Normal
9 | 1308 | 总压欠压恢复 | Battery under voltage recovery | 2 | 0 | 16 | V | 0.01 | 0 | 1 | IntParameterInfo | Normal
10 | 1309 | 总压欠压保护 | Battery under voltage protection | 2 | 0 | 18 | V | 0.01 | 0 | 1 | IntParameterInfo | Normal
11 | 130A | 单体高压恢复 | Cell high voltage recovery | 2 | 0 | 20 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
12 | 130B | 单体高压告警 | Cell high voltage alarm | 2 | 0 | 22 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
13 | 130C | 单体过压恢复 | Cell over voltage recovery | 2 | 0 | 24 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
14 | 130D | 单体过压保护 | Cell over voltage protection | 2 | 0 | 26 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
15 | 130E | 单体低压恢复 | Cell low voltage recovery | 2 | 0 | 28 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
16 | 130F | 单体低压告警 | Cell low voltage alarm | 2 | 0 | 30 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
17 | 1310 | 单体欠压恢复 | Cell under voltage recovery | 2 | 0 | 32 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
18 | 1311 | 单体欠压保护 | Cell under voltage protection | 2 | 0 | 34 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
19 | 1312 | 电芯欠压失效 | Cell under voltage failure | 2 | 0 | 36 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
20 | 1313 | 单体压差保护 | Cell diff pressure protection | 2 | 0 | 38 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
21 | 1314 | 压差保护恢复 | Diff pressure protection recovery | 2 | 0 | 40 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
22 | 1315 | 充电过流恢复 | Charge over current recovery | 2 | 0 | 42 | A | 1 | 1 | 1 | IntParameterInfo | Normal
23 | 1316 | 充电过流告警 | Charge over current alarm | 2 | 0 | 44 | A | 1 | 1 | 1 | IntParameterInfo | Normal
24 | 1317 | 充电过流保护 | Charge over current protection | 2 | 0 | 46 | A | 1 | 1 | 1 | IntParameterInfo | Normal
25 | 1318 | 充电过流延时 | Charge over current delay | 2 | 0 | 48 | s | 0.1 | 0 | 1 | IntParameterInfo | Normal
26 | 1319 | 充电二级过流保护 | Secondary charge over current protection | 2 | 0 | 50 | A | 1 | 1 | 1 | IntParameterInfo | Normal
27 | 131A | 充电二级过流延时 | Secondary charge over current delay | 2 | 0 | 52 | ms | 1 | 0 | 1 | IntParameterInfo | Normal
28 | 131B | 放电过流恢复 | Discharge over current recovery | 2 | 0 | 54 | A | 1 | 1 | 1 | IntParameterInfo | Normal
29 | 131C | 放电过流告警 | Discharge over current alarm | 2 | 0 | 56 | A | 1 | 1 | 1 | IntParameterInfo | Normal
30 | 131D | 放电过流保护 | Discharge over current protection | 2 | 0 | 58 | A | 1 | 1 | 1 | IntParameterInfo | Normal
31 | 131E | 放电过流延时 | Discharge over current delay | 2 | 0 | 60 | s | 0.1 | 0 | 1 | IntParameterInfo | Normal
32 | 131F | 放电二级过流保护 | Secondary discharge over current protection | 2 | 0 | 62 | A | 1 | 1 | 1 | IntParameterInfo | Normal
33 | 1320 | 放电二级过流延时 | Secondary discharge over current delay | 2 | 0 | 64 | ms | 1 | 0 | 1 | IntParameterInfo | Normal
34 | 1321 | 输出短路保护 | Output short-circuit protection | 2 | 0 | 66 | A | 1 | 1 | 0 | IntParameterInfo | Normal
35 | 1322 | 输出短路延时 | Output short-circuit delay | 2 | 0 | 68 | us | 1 | 0 | 0 | IntParameterInfo | Normal
36 | 1323 | 过流恢复延时 | Over current recovery delay | 2 | 0 | 70 | s | 0.1 | 0 | 1 | IntParameterInfo | Normal
37 | 1324 | 过流锁定次数 | Number of over current lock times | 2 | 0 | 72 | times | 1 | 0 | 1 | IntParameterInfo | Normal
38 | 1325 | 充电限流持续时间 | Charge current Limit duration | 2 | 0 | 74 | s | 0.1 | 0 | 1 | IntParameterInfo | Normal
39 | 1326 | 脉冲限流电流 | Pluse current limiting current | 2 | 0 | 76 | A | 1 | 0 | 1 | IntParameterInfo | Normal
40 | 1327 | 脉冲限流时间 | Pluse current limiting time | 2 | 0 | 78 | s | 0.1 | 0 | 1 | IntParameterInfo | Normal
41 | 1328 | 浮充锁定电压 | Float charge locking voltage | 2 | 0 | 80 | V | 0.001 | 0 | 0 | IntParameterInfo | Normal
42 | 1329 | 浮充解除电压 | Float charge release voltage | 2 | 0 | 82 | V | 0.001 | 0 | 0 | IntParameterInfo | Normal
43 | 132A | 浮充锁定电流 | Float charge locking current | 2 | 0 | 84 | mA | 1 | 0 | 0 | IntParameterInfo | Normal
44 | 132B | 短路预充完成率 | Short-circuit precharge completion rate | 2 | 0 | 86 | % | 0.1 | 0 | 1 | IntParameterInfo | Normal
45 | 132C | 正常预充完成率 | Normal precharge completion rate | 2 | 0 | 88 | % | 0.1 | 0 | 1 | IntParameterInfo | Normal
46 | 132D | 异常预充完成率 | Abnormal precharge completion rate | 2 | 0 | 90 | % | 0.1 | 0 | 1 | IntParameterInfo | Normal
47 | 132E | 预充超时时间 | Precharge over time | 2 | 0 | 92 | s | 0.1 | 0 | 1 | IntParameterInfo | Normal
48 | 132F | 充电高温恢复 | Charge high temperature recovery | 2 | 0 | 94 | ℃ | 0.1 | 1 | 1 | IntParameterInfo | Normal
49 | 1330 | 充电高温告警 | Charge high temperature alarm | 2 | 0 | 96 | ℃ | 0.1 | 1 | 1 | IntParameterInfo | Normal
50 | 1331 | 充电过温恢复 | Charge over temperature recovery | 2 | 0 | 98 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
51 | 1332 | 充电过温保护 | Charge over temperature protection | 2 | 0 | 100 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
52 | 1333 | 充电低温恢复 | Charge low temperature recovery | 2 | 0 | 102 | ℃ | 0.1 | 1 | 1 | IntParameterInfo | Normal
53 | 1334 | 充电低温告警 | Charge low temperature alarm | 2 | 0 | 104 | ℃ | 0.1 | 1 | 1 | IntParameterInfo | Normal
54 | 1335 | 充电欠温恢复 | Charge under temperature recovery | 2 | 0 | 106 | ℃ | 0.1 | 1 | 1 | IntParameterInfo | Normal
55 | 1336 | 充电欠温保护 | Charge under temperature protection | 2 | 0 | 108 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
56 | 1337 | 放电高温恢复 | Discharge high temperature recovery | 2 | 0 | 110 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
57 | 1338 | 放电高温告警 | Discharge high temperature alarm | 2 | 0 | 112 | ℃ | 0.1 | 1 | 1 | IntParameterInfo | Normal
58 | 1339 | 放电过温恢复 | Discharge over temperature recovery | 2 | 0 | 114 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
59 | 133A | 放电过温保护 | Discharge over temperature protection | 2 | 0 | 116 | ℃ | 0.1 | 1 | 1 | IntParameterInfo | Normal
60 | 133B | 放电低温恢复 | Discharge low temperature recovery | 2 | 0 | 118 | ℃ | 0.1 | 1 | 1 | IntParameterInfo | Normal
61 | 133C | 放电低温告警 | Discharge low temperature alarm | 2 | 0 | 120 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
62 | 133D | 放电欠温恢复 | Discharge under temperature recovery | 2 | 0 | 122 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
63 | 133E | 放电欠温保护 | Discharge under temperature protection | 2 | 0 | 124 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
64 | 133F | 环境高温恢复 | High ambient temperature recovery | 2 | 0 | 126 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
65 | 1340 | 环境高温告警 | High ambient temperature alarm | 2 | 0 | 128 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
66 | 1341 | 环境过温恢复 | Over ambient temperature recovery | 2 | 0 | 130 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
67 | 1342 | 环境过温保护 | Over ambient temperature protection | 2 | 0 | 132 | ℃ | 0.1 | 1 | 1 | IntParameterInfo | Normal
68 | 1343 | 环境低温恢复 | Low ambient temperature recovery | 2 | 0 | 134 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
69 | 1344 | 环境低温告警 | Low ambient temperature alarm | 2 | 0 | 136 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
70 | 1345 | 环境欠温恢复 | Under ambient temperature recovery | 2 | 0 | 138 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
71 | 1346 | 环境欠温保护 | Under ambient temperature protection | 2 | 0 | 140 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
72 | 1347 | 功率高温恢复 | Power high temperature recovery | 2 | 0 | 142 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
73 | 1348 | 功率高温告警 | power high temperature alarm | 2 | 0 | 144 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
74 | 1349 | 功率过温恢复 | Power over temperature recovery | 2 | 0 | 146 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
75 | 134A | 功率过温保护 | Power over temperature protection | 2 | 0 | 148 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
76 | 134B | 温度调节关闭 | Temperature regulate stop | 2 | 0 | 150 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
77 | 134C | 温度调节开启 | Temperature regulate open | 2 | 0 | 152 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
78 | 134D | 均衡高温禁止 | Equalization high temperature prohibition | 2 | 0 | 154 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
79 | 134E | 均衡低温禁止 | Equalization low temperature prohibition | 2 | 0 | 156 | ℃ | 0.1 | 0 | 1 | IntParameterInfo | Normal
80 | 134F | 静态均衡定时 | Static equalization timing | 2 | 0 | 158 | H | 1 | 0 | 1 | IntParameterInfo | Normal
81 | 1350 | 均衡开启电压 | Equalization open voltage | 2 | 0 | 160 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
82 | 1351 | 均衡开启压差 | Equalization open difference pressure | 2 | 0 | 162 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
83 | 1352 | 均衡结束压差 | Equalization stop difference pressure | 2 | 0 | 164 | V | 0.001 | 0 | 1 | IntParameterInfo | Normal
84 | 1353 | 补电 SOC | Power supply SOC | 2 | 0 | 166 | % | 0.1 | 0 | 1 | IntParameterInfo | Normal
85 | 1354 | SOC低恢复 | SOC low recovery | 2 | 0 | 168 | % | 0.1 | 0 | 1 | IntParameterInfo | Normal
86 | 1355 | SOC低告警 | SOC low alarm | 2 | 0 | 170 | % | 0.1 | 0 | 1 | IntParameterInfo | Normal
87 | 1356 | SOC保护恢复 | SOC protection recovery | 2 | 0 | 172 | % | 0.1 | 0 | 1 | IntParameterInfo | Normal
88 | 1357 | SOC低保护 | SOC low protection | 2 | 0 | 174 | % | 0.1 | 0 | 1 | IntParameterInfo | Normal
89 | 1358 | 电池额定容量 | Rated battery capacity | 2 | 0 | 176 | Ah | 0.01 | 0 | 1 | IntParameterInfo | Normal
90 | 1359 | 电池总容量 | Total battery capacity | 2 | 0 | 178 | Ah | 0.01 | 0 | 1 | IntParameterInfo | Normal
91 | 135A | 电池剩余容量 | Battery remaining capacity | 2 | 0 | 180 | Ah | 0.01 | 0 | 1 | IntParameterInfo | Normal
92 | 135B | 待机休眠定时 | Stand-by time | 2 | 0 | 182 | H | 1 | 0 | 1 | IntParameterInfo | Normal
93 | 135C | 强制输出延迟 | Forced output delay | 2 | 0 | 184 | s | 0.1 | 0 | 1 | IntParameterInfo | Normal
94 | 135D | 强制输出间隔 | Forced output splite | 2 | 0 | 186 | Min | 1 | 0 | 1 | IntParameterInfo | Normal
95 | 135E | 强制输出次数 | Number of forced output | 2 | 0 | 188 | times | 1 | 0 | 1 | IntParameterInfo | Normal
96 | 135F | 补偿位点1 | Compensation site 1 | 2 | 0 | 190 | Cell | 1 | 0 | 1 | IntParameterInfo | Normal
97 | 1360 | 补偿位点1电阻 | Compensation site 1 resistance | 2 | 0 | 192 | mΩ | 1 | 0 | 1 | IntParameterInfo | Normal
98 | 1361 | 补偿位点2 | Compensating site 2 | 2 | 0 | 194 | Cell | 1 | 0 | 1 | IntParameterInfo | Normal
99 | 1362 | 补偿位点2电阻 | Compensation site 2 resistance | 2 | 0 | 196 | mΩ | 1 | 0 | 1 | IntParameterInfo | Normal
100 | 1363 | 单体压差告警 | Cell diff pressure alarm | 2 | 0 | 198 | mV | 1 | 0 | 1 | IntParameterInfo | Normal
101 | 1364 | 压差告警恢复 | Diff pressure alarm recovery | 2 | 0 | 200 | mV | 1 | 0 | 1 | IntParameterInfo | Normal
102 | 1365 | 充电请求电压 | Charging request voltage | 2 | 0 | 202 | V | 0.01 | 0 | 1 | IntParameterInfo | Normal
103 | 1366 | 充电请求电流 | Charging request current | 2 | 0 | 204 | A | 1 | 0 | 1 | IntParameterInfo | Normal
104 | 1367 | 放电请求电流 | Discharge request current | 2 | 0 | 206 | A | 1 | 0 | 1 | IntParameterInfo | Normal
105 | 1368 | PCS协议 | Pcs protocol | 2 | 0 | 208 | PPT | 1 | 0 | 0 | IntParameterInfo | Normal
106 | 1369 | 检流器校正因子 | Current detector correction factor | 2 | 0 | 210 | 0.1 | 1 | 0 | 0 | IntParameterInfo | Normal

## SFA
ID | rtuAddress | description zh-CN | description en-US | bit | bitIndex | byteIndex | isDisplay | datatype
1 | 1400 | 单体高压告警 | Cell high voltage alarm | 1 | 0 | 0 | 1 | SwitchParameterInfo
2 | 1401 | 单体过压保护 | Cell over voltage protection | 1 | 1 | 0 | 1 | SwitchParameterInfo
3 | 1402 | 单体低压告警 | Cell low voltage alarm | 1 | 2 | 0 | 1 | SwitchParameterInfo
4 | 1403 | 单体欠压保护 | Cell under voltage protection | 1 | 3 | 0 | 1 | SwitchParameterInfo
5 | 1404 | 总压高压告警 | Battery high voltage alarm | 1 | 4 | 0 | 1 | SwitchParameterInfo
6 | 1405 | 总压过压保护 | Battery over voltage protection | 1 | 5 | 0 | 1 | SwitchParameterInfo
7 | 1406 | 总压低压告警 | Battery low voltage alarm | 1 | 6 | 0 | 1 | SwitchParameterInfo
8 | 1407 | 总压欠压保护 | Battery under voltage protection | 1 | 7 | 0 | 1 | SwitchParameterInfo
9 | 1408 | 充电高温告警 | Charge high temperature alarm | 1 | 0 | 1 | 1 | SwitchParameterInfo
10 | 1409 | 充电过温保护 | Charge over temperature protection | 1 | 1 | 1 | 1 | SwitchParameterInfo
11 | 140A | 充电低温告警 | Charge low temperature alarm | 1 | 2 | 1 | 1 | SwitchParameterInfo
12 | 140B | 充电欠温保护 | Charge under temperature protection | 1 | 3 | 1 | 1 | SwitchParameterInfo
13 | 140C | 放电高温告警 | Discharge high temperature alarm | 1 | 4 | 1 | 1 | SwitchParameterInfo
14 | 140D | 放电过温保护 | Discharge over temperature protection | 1 | 5 | 1 | 1 | SwitchParameterInfo
15 | 140E | 放电低温告警 | Discharge low temperature alarm | 1 | 6 | 1 | 1 | SwitchParameterInfo
16 | 140F | 放电欠温保护 | Discharge under temperature protection | 1 | 7 | 1 | 1 | SwitchParameterInfo
17 | 1410 | 环境高温告警 | High ambient temperature alarm | 1 | 0 | 2 | 1 | SwitchParameterInfo
18 | 1411 | 环境过温保护 | Over ambient temperature protection | 1 | 1 | 2 | 1 | SwitchParameterInfo
19 | 1412 | 环境低温告警 | Low ambient temperature alarm | 1 | 2 | 2 | 1 | SwitchParameterInfo
20 | 1413 | 环境欠温保护 | Under ambient temperature protection | 1 | 3 | 2 | 1 | SwitchParameterInfo
21 | 1414 | 功率高温告警 | Power high temperature alarm | 1 | 4 | 2 | 1 | SwitchParameterInfo
22 | 1415 | 功率过温保护 | Power over temperature protection | 1 | 5 | 2 | 1 | SwitchParameterInfo
23 | 1416 | 电芯低温加热 | Cell temperature low heating | 1 | 6 | 2 | 1 | SwitchParameterInfo
24 | 1417 | 电芯电压失效 | Cell voltage fault | 1 | 7 | 2 | 0 | SwitchParameterInfo
25 | 1418 | 强制输出功能 | Forced output | 1 | 0 | 3 | 1 | SwitchParameterInfo
26 | 1419 | 散热开启 | Heat dissipation turned on | 1 | 1 | 3 | 1 | SwitchParameterInfo
27 | 141A | 容量灯常亮 | CapLeds idle display | 1 | 2 | 3 | 1 | SwitchParameterInfo
28 | 141B | 保留 | Reservation | 1 | 3 | 3 | 0 | SwitchParameterInfo
29 | 141C | 保留 | Reservation | 1 | 4 | 3 | 0 | SwitchParameterInfo
30 | 141D | 保留 | Reservation | 1 | 5 | 3 | 0 | SwitchParameterInfo
31 | 141E | 保留 | Reservation | 1 | 6 | 3 | 0 | SwitchParameterInfo
32 | 141F | 保留 | Reservation | 1 | 7 | 3 | 0 | SwitchParameterInfo
33 | 1420 | 充电电流告警 | Charge current alarm | 1 | 0 | 4 | 1 | SwitchParameterInfo
34 | 1421 | 充电过流保护 | Charge over current protection | 1 | 1 | 4 | 1 | SwitchParameterInfo
35 | 1422 | 充电过流二级保护 | Secondary charge over current protection | 1 | 2 | 4 | 1 | SwitchParameterInfo
36 | 1423 | 放电电流告警 | Discharge current alarm | 1 | 3 | 4 | 1 | SwitchParameterInfo
37 | 1424 | 放电过流保护 | Discharge over current protection | 1 | 4 | 4 | 1 | SwitchParameterInfo
38 | 1425 | 放电二级过流保护 | Secondary discharge over current protection | 1 | 5 | 4 | 1 | SwitchParameterInfo
39 | 1426 | 输出短路保护 | Output short-circuit protection | 1 | 6 | 4 | 1 | SwitchParameterInfo
40 | 1427 | 保留 | Reservation | 1 | 7 | 4 | 0 | SwitchParameterInfo
41 | 1428 | 输出短路锁定 | Output short-circuit lock | 1 | 0 | 5 | 1 | SwitchParameterInfo
42 | 1429 | 反接保护 | Inverse current protection | 1 | 1 | 5 | 0 | SwitchParameterInfo
43 | 142A | 充电二级过流锁定 | Secondary charge over current lock | 1 | 2 | 5 | 1 | SwitchParameterInfo
44 | 142B | 放电二级过流锁定 | Secondary discharge over current lock | 1 | 3 | 5 | 1 | SwitchParameterInfo
45 | 142C | 保留 | Reservation | 1 | 4 | 5 | 0 | SwitchParameterInfo
46 | 142D | 保留 | Reservation | 1 | 5 | 5 | 0 | SwitchParameterInfo
47 | 142E | 保留 | Reservation | 1 | 6 | 5 | 0 | SwitchParameterInfo
48 | 142F | 保留 | Reservation | 1 | 7 | 5 | 0 | SwitchParameterInfo
49 | 1430 | SOC低告警 | Low SOC alarm | 1 | 0 | 6 | 1 | SwitchParameterInfo
50 | 1431 | 间歇式的充电 | Intermittent charge | 1 | 1 | 6 | 1 | SwitchParameterInfo
51 | 1432 | 外部开关控制 | External switch control | 1 | 2 | 6 | 1 | SwitchParameterInfo
52 | 1433 | 静态待机休眠 | Static stand-by sleep | 1 | 3 | 6 | 1 | SwitchParameterInfo
53 | 1434 | 历史数据记录 | History data recording | 1 | 4 | 6 | 1 | SwitchParameterInfo
54 | 1435 | SOC低保护 | Under SOC protect | 1 | 5 | 6 | 1 | SwitchParameterInfo
55 | 1436 | 主动限流 | Active-limited current | 1 | 6 | 6 | 1 | SwitchParameterInfo
56 | 1437 | 被动限流 | Passive-limited current | 1 | 7 | 6 | 1 | SwitchParameterInfo
57 | 1438 | 均衡模块开启 | Equilibrium module to open | 1 | 0 | 7 | 1 | SwitchParameterInfo
58 | 1439 | 静态均衡指示 | Static equilibrium indicate | 1 | 1 | 7 | 1 | SwitchParameterInfo
59 | 143A | 静态均衡超时 | Static equilibrium overtime | 1 | 2 | 7 | 1 | SwitchParameterInfo
60 | 143B | 超温禁止均衡 | Equalization temperature limit | 1 | 3 | 7 | 1 | SwitchParameterInfo
61 | 143C | 保留 | Reservation | 1 | 4 | 7 | 0 | SwitchParameterInfo
62 | 143D | 保留 | Reservation | 1 | 5 | 7 | 0 | SwitchParameterInfo
63 | 143E | 保留 | Reservation | 1 | 6 | 7 | 0 | SwitchParameterInfo
64 | 143F | 保留 | Reservation | 1 | 7 | 7 | 0 | SwitchParameterInfo
65 | 1440 | 蜂鸣器声指示 | Buzzer indicator | 1 | 0 | 8 | 0 | SwitchParameterInfo
66 | 1441 | LCD显示功能 | LCD display | 1 | 1 | 8 | 1 | SwitchParameterInfo
67 | 1442 | 手动强制输出 | Manual forced output | 1 | 2 | 8 | 0 | SwitchParameterInfo
68 | 1443 | 自动强制输出 | Auto forced output | 1 | 3 | 8 | 0 | SwitchParameterInfo
69 | 1444 | 欠压恢复功能 | Under voltage recover | 1 | 4 | 8 | 0 | SwitchParameterInfo
70 | 1445 | 气溶胶检测功能 | Aerosol detection function | 1 | 5 | 8 | 1 | SwitchParameterInfo
71 | 1446 | 气溶胶常断模式 | Aerosol normally disconnected mode | 1 | 6 | 8 | 1 | SwitchParameterInfo
72 | 1447 | 检流器温度补偿 | Current detector temperature compensation | 1 | 7 | 8 | 1 | SwitchParameterInfo
73 | 1448 | NTC失效 | NTC failure | 1 | 0 | 9 | 1 | SwitchParameterInfo
74 | 1449 | AFE失效 | AFE failure | 1 | 1 | 9 | 1 | SwitchParameterInfo
75 | 144A | 充电管失效 | Charge mosfets failure | 1 | 2 | 9 | 1 | SwitchParameterInfo
76 | 144B | 放电管失效 | Discharge mosfets failure | 1 | 3 | 9 | 1 | SwitchParameterInfo
77 | 144C | 电芯压差失效 | Cell diff failure | 1 | 4 | 9 | 1 | SwitchParameterInfo
78 | 144D | 断线 | Cell break | 1 | 5 | 9 | 1 | SwitchParameterInfo
79 | 144E | 按键失效 | Key failure | 1 | 6 | 9 | 1 | SwitchParameterInfo
80 | 144F | 保留 | Reservation | 1 | 7 | 9 | 0 | SwitchParameterInfo

## SCA
ID | rtuAddress | description zh-CN | description en-US | byte | value | Index | unit | scale | hasSign | isDisplay | datatype | attribute
1 | 150D | 零点校准 | Calibration Zero | 2 | 0 | 0 | A | 0.01 | 1 | 1 | AdjustInfo | Other
2 | 150E | 电流校准 | Calibration Current | 2 | -50 | 1 | A | 0.01 | 1 | 1 | AdjustInfo | Normal
3 | 150F | 电芯电压校准 | Calibration Voltage | 2 | 3.3 | 2 | V | 0.001 | 0 | 1 | AdjustInfo | Normal
4 | 1510 | 放电管关闭 | Discharing FETs Off | 2 | 0 | 0 | - | 1 | 0 | 1 | ControlInfo | OnOff
5 | 1510 | 放电管取消关闭 | Discharing FETs On | 2 | 0 | 0 | - | 1 | 0 | 1 | ControlInfo | OffOn
6 | 1511 | 充电管关闭 | Charing FETs Off | 2 | 0 | 1 | - | 1 | 0 | 1 | ControlInfo | OnOff
7 | 1512 | 限流管关闭 | Current Limit FETs Off | 2 | 0 | 2 | - | 1 | 0 | 1 | ControlInfo | OnOff
8 | 1513 | 预充管开启 | Precharging FETs On | 2 | 0 | 3 | - | 1 | 0 | 0 | ControlInfo | OffOn
9 | 1514 | 加热管开启 | Heater FETs On | 2 | 0 | 4 | - | 1 | 0 | 1 | ControlInfo | OffOn
10 | 1515 | 充电管开启 | Charing FETs On | 2 | 0 | 5 | - | 1 | 0 | 1 | ControlInfo | OffOn
11 | 1516 | 恢复出厂 | Parameter Reset | 2 | 0 | 6 | - | 1 | 0 | 1 | ControlInfo | Simple
12 | 1517 | 系统关机 | System Power Off | 2 | 0 | 7 | - | 1 | 0 | 1 | ControlInfo | Simple
13 | 1518 | 系统复位 | System Reset | 2 | 0 | 8 | - | 1 | 0 | 1 | ControlInfo | Simple

## PCT
ID | protocolName | 字段1
0 | Pylon_CAN | 派能
1 | Growatt_CAN | 古瑞瓦特
2 | Goodwe_CAN | 固德威
3 | Sofar_CAN | 首航
4 | SMA_CAN | SMA
5 | Victron_CAN | Victron
6 | Studer_CAN | Studer
7 | Ginlong_CAN | 锦浪
8 | Voltronic_485 | 日月元
9 | Srne_485 | 硕日
10 | Growatt_485 | 古瑞瓦特
11 | Pylon_485 | 派能
12 | Deye(Pylon)_485 | 德业（派能）
13 | XZH(LCD02)_485 | 鑫智恒(LCD)
14 | GudE_485 | 固德
15 | NPP-IMB_485 | 视源

## BASIC
ID | name | value
1 | HostProtocolName | 48100-RTU
2 | HostProtocolVerStr | 0.1
3 | FreshMode | 1
4 | FreshDuty | 1
5 | CP_MeterTmprType | K
6 | CP_ParaTmprType | K
7 | HistoryPICDeviation | 4
8 | HistoryPIADeviation | 22
9 | HistoryPIBDeviation | 28
10 | HistoryTotalNum | 80
11 | AllowShowManufacInfo | 0